## Sheet1
Section | SectionOrder | QuestionID | QuestionText | QOrder | RefA1 | RefA2 | RefB1 | RefB2
MDF | 1 | q1 | Check to see if the room is rated for smoke, fire, or both. This will tell you if and what type of firestopping is required. | 1
MDF | 1 | q2 | Sealed Concrete Floor | 2
MDF | 1 | q3 | Building/Room Entrance conduits and sleeves - ceiling, floor and walls labeled with far end location, Extends into the room a minimum 4" AFS | 3
MDF | 1 | q4 | Fire alarm annunciator | 4
MDF | 1 | q5 | No piping, ductwork, power distribution unrelated to designated equipment | 5
MDF | 1 | q6 | Walls extend to deck, no drop ceiling | 6
MDF | 1 | q7 | ¾x4'x8' AC-grade Fire-arted plywood wrapped vertically around room, 1’AFF, 2 coats fire-rated paint, sides sealed | 7
MDF | 1 | q8 | 3’x7’ door, opens out | 8
MDF | 1 | q9 | Ladder rack around the room and to each equipment racks | 9
MDF | 1 | q10 | 4" sleeves rated for the room entering above ladder rack | 10
Mechanical | 2 | q1 | Primary HVAC (24x365) functional and stable at designed loads (64-81 °F). | 1
Mechanical | 2 | q2 | Redundant HVAC (MDF required, IDF optional). | 2
Mechanical | 2 | q3 | HVAC common service points located outside of room (VAV boxes, AHUs). | 3