## Sheet1
Section | SectionOrder | QuestionID | QuestionText | QOrder | RefA1 | RefA2 | RefB1 | RefB2
MDF | 1 | q1 | Check to see if the room is rated for smoke, fire, or both. This will tell you if and what type of firestopping is required. | 1
MDF | 1 | q2 | Sealed Concrete Floor | 2
MDF | 1 | q3 | Building/Room Entrance conduits and sleeves - ceiling, floor and walls labeled with far end location, Extends into the room a minimum 4" AFS | 3
MDF | 1 | q4 | Fire alarm annunciator | 4
MDF | 1 | q5 | No piping, ductwork, power distribution unrelated to designated equipment | 5
MDF | 1 | q6 | Walls extend to deck, no drop ceiling | 6
MDF | 1 | q7 | ¾x4'x8' AC-grade Fire-arted plywood wrapped vertically around room, 1’AFF, 2 coats fire-rated paint, sides sealed | 7
MDF | 1 | q8 | 3’x7’ door, opens out | 8
MDF | 1 | q9 | Ladder rack around the room and to each equipment racks | 9
MDF | 1 | q10 | 4" sleeves rated for the room entering above ladder rack | 10
Mechanical | 2 | q1 | Primary HVAC (24x365) functional and stable at designed loads (64-81 °F). | 1
Mechanical | 2 | q2 | Redundant HVAC (MDF required, IDF optional). | 2
Mechanical | 2 | q3 | HVAC common service points located outside of room (VAV boxes, AHUs). | 3
Plumbing | 3 | q1 | Sprinkler heads with cages positioned not over equipment racks Note: Drainage troughs are recommended for leak protection | 1
Electrical - Div 26 | 4 | q1 | Lighting - >50 ft-candles (FC) 3" AFF located 8'6" AFF (contractor provided test results) | 1
Electrical - Div 26 | 4 | q2 | Utility power per rack - two (2) dedicated 30A 208V receptacles (NEMA L6-30R) mounted 6" to 12" above finished floor within the rear of the vertical wire manager. | 2
Electrical - Div 26 | 4 | q3 | IF REQUIRED - Emergency power per rack - two (2) dedicated 30A 208V receptacles (NEMA L6-30R) mounted 12" to 18" above finished floor, wall-mounted OR within the rear of the vertical wire manager. (MDF router rack only or as included in design) | 3
Electrical - Div 26 | 4 | q4 | A minimum of two (2) dedicated convenience 20A 120V duplex receptacles (NEMA 5-20R) mounted 6" above finished floor. Additional convenience duplex outlets shall be place at 6ft intervals around perimeter walls. | 4
Electrical - Div 26 | 4 | q5 | Rack mounted ATS and PDUs installed and energized. | 5
Electrical - Div 26 | 4 | q6 | Breaker panel schedule located in the room and clearly identified. | 6
Electrical - Div 26 | 4 | q7 | All receptacles labeled. | 7
Equipment Racks and Cabinets | 5 | q1 | Racks, cabinets assmbled correctly to manufacturer's specification, anchored securely to floor at all attachment points. | 1
Equipment Racks and Cabinets | 5 | q2 | Vertical wire managers on each side of equipment rack | 2
Equipment Racks and Cabinets | 5 | q3 | Radius drops positioned on ladder rack above equipment racks to route cables into vertical managers | 3
Equipment Racks and Cabinets | 5 | q4 | Vertical rack busbar (RBC), with insulator stand-offs | 4
Bonding and Grounding | 6 | q1 | BICSI hole pattern busbar, sized minimum 4"x20: for MDF, 12"x4" for IDF, connected with a bonding conductor one gauge size smaller than the the Main electrical,attached either exothermically welded or with a two-hole lug with anti-oxidant paste. (Primary Busbar (PBB) in MDF, Secondary Busbar (SBB) in IDF) | 1
Bonding and Grounding | 6 | q2 | #4 AWG green-jacketed bonding conductor Telecommunications Equipment Bonding Busbar (TEBC) from the PBB/SBB run along the ladder rack over the equipment racks, terminated with 2-hole lugs. | 2
Bonding and Grounding | 6 | q3 | #6 AWG green-jacketed bonding conductor from the TEBC, bonded with an irreversable lug, to the equipment rack and a secod to the vertical rack bus bar (RBB) | 3
Horizontal Cabling and Pathways | 7 | q1 | Start at the TR. The cables should enter the room through a conduit or sleeve, be supported either bu cable tray or ladder tray to the equipment racks, where it is dropped into the vertical wire managers and routed to the patch panels where it will terminate. | 1 | CA Images/Picture1.png |  | CA Images/Picture2.png
Horizontal Cabling and Pathways | 7 | q2 | Cat 6 or 6A - check the cable markings. Look for CMR rating for using in non-plenum spaces or CMP for plenum spaces, manufacturer name and electrical characteristics (UL or ETL) to confirm it meets drawings and spec requirments. | 2 | CA Images/Picture3.png
Horizontal Cabling and Pathways | 7 | q3 | 10' service loop laid out on on the ladder tray over the equipment racks. | 3
Horizontal Cabling and Pathways | 7 | q4 | Cables will leave the room either through conduits, sleeves or on cable tray through a firestopped hole provided by the GC. | 4 | CA Images/Picture4.png
Horizontal Cabling and Pathways | 7 | q5 | Sleeves - cable will be supported by j-hooks, sized to accommodate the number of cables it needs to support. | 5 | CA Images/Picture5.png
Horizontal Cabling and Pathways | 7 | q6 | No kinks, excessive bends, scuffed or damaged jacket | 6
Horizontal Cabling and Pathways | 7 | q7 | No paint on cable. If found, must be replaced. | 7 | CA Images/Picture6.png
Horizontal Cabling and Pathways | 7 | q8 | 3' Service loop at cable stubout or stubup, supported by a j-hook. Attaching to the stubout is not acceptable. | 8
Horizontal Cabling and Pathways | 7 | q9 | Cables wil be home run with no slices between patch panel and WAO jack. | 9